{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["Velocity","cfm"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":5,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Velocity","index":0,"n_rows":28,"n_cols":40,"rows_kept":28,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[5,1,5,7],[9,1,9,5],[9,7,9,11]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"S480HZ or VZ Return Grille / 0 deg deflection, 3/8\" spacing"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},20,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},18,"Inches",{"$nulls":11},2.5,2.3059895833333335,0.75]
[null,"Enter Minimum Neck Velocity (greater than 0)=",{"$nulls":6},400,"FPM",{"$nulls":22},"New Version!"]
[null,"Enter Maximum Neck Velocity =",{"$nulls":6},1100,"FPM"]
[{"$nulls":26},"Pressure Constants",null,null,null," ",null,"Constants from Titus 30R Catalog"]
[{"$nulls":27},"m","b",null," "," "]
[null,"S480HZ or VZ Return Grille / 0 deg deflection",{"$nulls":24},"0 deg",0,3.25,"Modified to agree with Titus"]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","From S480Z - Titus version sound regression.xls"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",10.20107373683118,10.201073736831187,10.201073736831223,10.20107373683145,10.201073736831662,10.210736005948204]
[null,null,null,400,922.3958333333334,-0.022443855293242998,17.825148616455444,null,null,2.032,435.32231531250005,-5.588519968017507,35.19205179292241,33.393571896331835,34.275966621397274,26.614640286244576,18.370405963363954,12.636674970845057,{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",44.987614680952476,37.30176468528894,36.47758021710292,54.69615336661586,74.47683562233769,78.38885999777882]
[null,null,null,487.5,1124.169921875,-0.03333701552834238,22.25962676656659,null,null,2.4765,530.5490717871094,-8.300916866557253,39.05714600463172,36.59833915936915,37.40992438186464,31.313839994416252,24.76905564309907,19.371424772287348,{"$nulls":8},"0 Deg",null,-120.10858737958739,51.614937023767276,10,null,"B",-85.56995496677152,-67.36939209029781,-64.34241993509163,-119.40956656167391,-179.12432278333932,-195.04088191357454]
[null,null,null,575,1325.9440104166667,-0.046378122852052894,25.960068042169077,null,null,2.9210000000000003,625.7758282617189,-11.548152590161171,42.28245317064919,39.272622954982296,40.02511973524291,35.235183605497454,30.108540150970402,24.991374922563317]
[null,20,null,662.5,1527.7180989583335,-0.061567177264374585,29.13531769519509,508,null,3.3655000000000004,721.0025847363282,-15.330227138829272,45.05000295648705,41.567354329345534,42.26914889823985,38.59998364234012,34.6902089488885,29.8137037843507]
[null,"x",2.5,750,1729.4921875,-0.07890417876530742,31.916092081433625,"x",0.2322576,3.81,816.2293412109375,-19.64714051256155,47.47372782793572,43.57700110563792,44.234392422473405,41.54675973232399,38.70267682754401,34.03693346586493,{"$nulls":8}," "]
[null,18,null,837.5,1931.2662760416667,-0.09838912735485139,34.3896632162402,457.2,null,4.2545,911.456097685547,-24.498892711357996,49.62969413372359,45.36463417705659,45.98252764641195,44.167993699737636,42.27187135590934,37.79360609905276]
[null,null,null,925,2133.0403645833335,-0.12002202303300649,36.61720477089134,null,null,4.699000000000001,1006.6828541601564,-29.885483735218617,51.5712208878938,46.97446334065778,47.5567875493021,46.52851105244902,45.486061971530674,41.176627626064935]
[null,null,null,1012.5,2334.814453125,-0.14380286579977275,38.643261334373626,null,null,5.1435,1101.9096106347656,-35.806913584143416,53.33713318490551,48.43868066858556,48.9886529177473,48.675515522775854,48.409523479786415,44.25364899740287,{"$nulls":21}," "]
[null,null,null,1100,2536.588541666667,-0.1697316556551502,40.50127794098646,null,null,5.588,1197.1363671093752,-42.263182258132396,54.95658173970311,49.78145666014237,50.30176020258659,50.64444868695308,51.09051478527921,47.07546399995254]
[{"$nulls":26}," "," "]
[null,"1) Performance data does not include damper",{"$nulls":37}," "]
[null,"2) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991."]
[null,"3) All pressures are in inches of water (Pascals)"]
[null,"4) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[{"$nulls":27}," ",null,null," "]

{"sheet":"cfm","index":1,"n_rows":28,"n_cols":40,"rows_kept":28,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[5,1,5,7],[9,1,9,5],[9,7,9,11]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"S480HZ or VZ Return Grille / 0 deg deflection, 3/8\" spacing"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},18,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},18,"Inches",{"$nulls":11},2.25,2.06640625,0.75]
[null,"Enter Minimum Air Flow (must be greater than 0)=",{"$nulls":6},700,"CFM",{"$nulls":22},"New Version!"]
[null,"Enter Maximum Air Flow =",{"$nulls":6},2000,"CFM"]
[{"$nulls":26},"Pressure Constants",null,null,null," ",null,"Constants from Titus 30R Catalog"]
[{"$nulls":27},"m","b",null," "," "]
[null,"S480HZ or VZ Return Grille / 0 deg deflection",{"$nulls":24},"0 deg",0,3.25,"Modified to agree with Titus"]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","From S480Z - Titus version sound regression.xls"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",10.20107373683118,10.201073736831187,10.201073736831223,10.20107373683145,10.201073736831662,10.210736005948204]
[null,null,null,338.7523629489603,700,0.016096896211688215,13.623286997998264,null,null,1.7208620037807185,330.36318,4.008127156710366,31.45895529876152,30.21522205488195,31.15710448465155,22.180804206790466,12.508846564316961," - ",{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",44.987614680952476,37.30176468528894,36.47758021710292,54.69615336661586,74.47683562233769,78.38885999777882]
[null,null,null,417.39130434782606,862.5,0.02443792183158405,18.302752092984406,null,null,2.1203478260869564,407.0546325,6.085042536064428,35.53758030045948,33.597039720295726,34.464200709468976,27.139615653004764,19.260995705161,13.599111919965207,{"$nulls":8},"0 Deg",null,-120.10858737958739,51.614937023767276,10,null,"B",-85.56995496677152,-67.36939209029781,-64.34241993509163,-119.40956656167391,-179.12432278333932,-195.04088191357454]
[null,null,null,496.0302457466919,1025,0.034513880780418234,22.172053544368225,null,null,2.519833648393195,483.746085,8.59395631432414,38.91006611205994,36.3933576189208,37.19873381588378,31.239899753111413,24.84413393577224,19.47551412543653]
[null,18,null,574.6691871455577,1187.5,0.04632477305819074,25.470751415771105,457.2,null,2.919319470699433,560.4375375000001,11.534868491489494,41.78521345011086,38.77730418288297,39.530006954135935,34.73551739963301,29.60393009755193,24.4853267984095]
[null,"x",2.25,653.3081285444234,1350,0.05987059866490159,28.345711160460525,"x",0.20903184000000002,3.318805293005671,637.12899,14.907779067560496,44.29103034489425,40.855018078507825,41.561813651091875,37.78210135741193,33.75230102799548,28.851598074143748,{"$nulls":8}," "]
[null,18,null,731.9470699432892,1512.5,0.07515135760055075,30.893507801276627,457.2,null,3.718291115311909,713.8204425,18.71268804253714,46.51169165287341,42.69629341936371,43.362405915680704,40.48199181255009,37.428597901705324,32.720998788277754]
[null,null,null,810.586011342155,1675,0.09216704986513827,33.18105228892199,null,null,4.117776937618148,790.511895,22.949595416419427,48.505517004793106,44.34948629541013,44.979071407490785,42.90609404620375,40.72936865933885,36.19514822874207]
[null,null,null,889.2249527410208,1837.5,0.1109176754586641,35.25661982191548,null,null,4.517262759924386,867.2033475000001,27.61850118920736,50.314583096951864,45.849484864981164,46.44592742914828,45.105565103489084,43.72427112152027,39.34736311345351,{"$nulls":21}," "]
[null,null,null,967.8638941398866,2000,0.13140323438112833,37.156186175981844,null,null,4.916748582230625,943.8948,32.71940536090096,51.97024644026443,47.22228857703156,47.78839897040498,47.1185283777489,46.46521588021246,42.2322807278416]
[{"$nulls":26}," "," "]
[null,"1) Performance data does not include damper",{"$nulls":37}," "]
[null,"2) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991."]
[null,"3) All pressures are in inches of water (Pascals)"]
[null,"4) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[{"$nulls":27}," ",null,null," "]