{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["cfm"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"cfm","index":0,"n_rows":28,"n_cols":42,"rows_kept":28,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[9,1,9,5],[9,7,9,11],[5,2,5,4],[5,8,5,9],[8,1,8,5]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"S5480HZ or VZ Return Grille / 0 deg deflection"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},13,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},13,"Inches",{"$nulls":11},1.1736111111111112,0.87890625,1.75]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},800,"CFM"]
[null,"Series =","S5480 HZ or VZ",{"$nulls":4},"Tag =","Room 23"]
[{"$nulls":26},"Pressure Constants",null,null,null," ",null,"Constants from Titus 60F 0 defl / from 30R teams data "]
[null,"S5480 HZ or VZ Return Grille",{"$nulls":25},"m","b",null," "," "]
[null,"Tag : Room 23",{"$nulls":24},"0 deg",0,-1.0571428571428567]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24},"2002-11-21"]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","from S5480Z Sound Analysis.XLS"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7",null,null,"NC"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",6.3248056459018684,6.390259070510827,6.397277903298799,6.242126813335101,6.073672654657878,6.0379401739976455,null,"M(An)",6.886700876319359]
[null,"13 x 13",1.1736111111111112,910.2222222222222,800,-0.10625619982433326,29.71316560692267,"330 x 330",0.10903204000000001,4.623928888888889,377.55792,-26.457793756258983,44.66730897786379,40.16040397449573,40.75236343117709,39.511100063118526,38.23740204797355,33.87631503405318,{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",60.142884978123696,51.228458953959404,50.27252935917839,71.40332461263321,94.34593067124689,99.21251416032577,null,"M(Vn)",65.37330584697509]
[{"$nulls":26},"0 Deg",null,-163.35003378407086,65.37330584697509,6.886700876319359,null,"B",-132.94980233153294,-111.07393728630291,-107.65284776410829,-171.431947062907,-240.6056420401921,-259.3696701707514,null,"B",-163.35003378407086]
[]
[{"$nulls":28}," "," "]
[{"$nulls":26}," "]
[]
[]
[{"$nulls":39}," "]
[]
[{"$nulls":26}," "," "]
[{"$nulls":39}," "]
[]
[]
[]
[{"$nulls":27}," ",null,null," "]