{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["cfm"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"cfm","index":0,"n_rows":28,"n_cols":43,"rows_kept":28,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[9,1,9,5],[9,7,9,11],[5,2,5,4],[5,8,5,9],[8,1,8,5]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"S5480 H or V Return Grille / 30 deg deflection"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},13,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},13,"Inches",{"$nulls":11},1.1736111111111112,0.87890625,1.75]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},600,"CFM"]
[null,"Series =","S5480 H or V",{"$nulls":4},"Tag =","Room 23"]
[{"$nulls":26},"Pressure Constants",null,null,null," ",null,"Cosntants from Titus 355RLHD 40 defl"]
[null,"S5480 H or V Return Grille",{"$nulls":25},"m","b",null," "," "]
[null,"Tag : Room 23",{"$nulls":24},"30 deg",0,-2.528571428571428]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24},"2002-11-21"]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","from S5480 Sound Analysis.XLS"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7",null,null,"NC"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",11.207399265464796,11.108823296335114,11.098252600479919,11.331917517878216,11.585617489189525,11.639432303792999,null,"M(An)",11.948104701021213]
[null,"13 x 13",1.1736111111111112,682.6666666666666,600,-0.10252063029925906,28.386081549789598,"330 x 330",0.10903204000000001,3.4679466666666667,283.16844000000003,-25.527636944515507,42.99658486774392,39.54533200009482,40.25049326198408,36.50690735759148,32.51633099053885,27.578939990251335,{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",66.72186301644962,57.033829212724285,55.99494255831443,78.95950114684788,103.89310230511572,109.18201549179177,null,"M(Vn)",73.4073344724104,"Adjust"]
[{"$nulls":26},"30 Deg",null,-178.99584402995995,73.4073344724104,11.948104701021213,null,"B",-145.47884141991597,-121.47771053574237,-117.82872024834539,-186.6455591817702,-261.28894304093274,-281.2132010745367,null,"B",-179.99584402995995,1]
[]
[]
[{"$nulls":26}," "]
[]
[]
[{"$nulls":39}," "]
[]
[{"$nulls":26}," "," "]
[{"$nulls":39}," "]
[]
[]
[]
[{"$nulls":27}," ",null,null," "]