{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["cfm range"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"cfm range","index":0,"n_rows":30,"n_cols":40,"rows_kept":30,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[5,1,5,7],[9,1,9,5],[9,7,9,11]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"600 / 600A / 600C / 5600 / 5600A Door Grille"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},20,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null,"Based on Titus T-700 - 50711701.xls"]
[null,"Enter Duct Height in inches =",{"$nulls":6},30,"Inches",{"$nulls":11},4.166666666666667,3.91015625,0.75]
[null,"Enter Minimum Air Flow (must be greater than 0)=",{"$nulls":6},350,"CFM"]
[null,"Enter Maximum Air Flow =",{"$nulls":6},1350,"CFM"]
[{"$nulls":26},"Pressure Constants",null,null,null," "]
[{"$nulls":27},"m","b",null," "," "]
[null,"600 / 600A / 600C / 5600 / 5600A Door Grille",{"$nulls":24},"0 Degrees",0,-11.3]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","based on s80 / adjusted to Titus catalog NC values."]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",9.753013027537682,9.753013027537703,9.753013027537708,9.753013027537703,9.753013027537696,9.7530130275377]
[null,null,null,89.5104895104895,350,0.0061439537100853436,11.326486009560668,null,null,0.4547132867132867,165.18159,1.5298444738112504,53.13950277850812,19.977275886201046,13.265945856665565," - "," - "," - ",{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",-5.334008073245482,30.744139414847908,34.3285351004995,43.53792844512962,39.66120807631725,40.1601536140089]
[null,null,null,121.47852147852147,475,0.011316159639493922,17.722634841238488,null,null,0.6171108891108891,224.175015,2.8177237502339865,52.4320769426147,24.054734754976092,17.81878722941795," - "," - "," - ",{"$nulls":8},"0 deg",null,-88.72871022823963,48.22711834204125,10,null,"B",57.77513719992817,-45.807085295834995,-59.51470382682234,-93.71293688551766,-88.41143050570288,-95.51745777861296]
[null,null,null,153.44655344655345,600,0.01805570069902632,22.615644488816343,null,null,0.7795084915084916,283.16844000000003,4.495869474057554,51.890901067714935,27.17396260716549,21.3016794114195," - "," - "," - "]
[null,20,null,185.41458541458542,725,0.026362576888682526,26.579274905612166,508,null,0.941906093906094,342.16186500000003,6.564281645281949,51.452516246697755,29.70072369744349,24.12303035599315,10.813026583081093," - "," - "]
[null,"x",4.166666666666667,217.38261738261738,850,0.036236788208462545,29.910848568313014,"x",0.38709600000000005,1.1043036963036963,401.15529000000004,9.022960263907173,51.084038066280186,31.82455710649091,26.494477113578654,13.820666697665825," - "," - ",{"$nulls":8}," ",{"$nulls":4},"From S80P Sound Analysis.xls"]
[null,30,null,249.35064935064935,975,0.04767833465836637,32.784494690675345,762,null,1.2667012987012987,460.14871500000004,11.871905329933226,50.766207514854315,33.65646786649642,28.539966563690257,16.41490420455352,12.424646485145976," - ",{"$nulls":13},"Band","Const","Slope 1","Slope 2","NC"]
[null,null,null,281.31868131868134,1100,0.06068721623839403,35.311020316218816,null,null,1.4290989010989013,519.14214,15.111116843360113,50.4867691294146,35.26709397763981,30.33837224498457,18.695772224067905,14.502420608703224," - ",{"$nulls":13},2,57.77513719992817,-5.334008073245482,9.753013027537682,10]
[null,null,null,313.2867132867133,1225,0.07526343294854546,37.56531997056436,null,null,1.5914965034965036,578.135565,18.74059480418782,50.23743943754886,36.70417969286958,31.94300481420413,20.730883182775525,16.356320462790684," - ",{"$nulls":13},3,-45.807085295834995,30.744139414847908,9.753013027537703,35.680029057786996," ",null,null," "]
[null,null,null,345.2547452547453,1350,0.09140698478882076,39.60039246777109,null,null,1.753894105894106,637.12899,22.76033921241637,50.012356672853,38.0015110434534,33.3915893461877,22.568082746216984,18.02993142145636,12.190297604109112,{"$nulls":13},4,-59.51470382682234,34.3285351004995,9.753013027537708,-78.94438574956783]
[{"$nulls":26}," "," ",null,null,null,5,-93.71293688551766,43.53792844512962,9.753013027537703]
[{"$nulls":31},6,-88.41143050570288,39.66120807631725,9.753013027537696,{"$nulls":4}," "]
[null,"1) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991.",{"$nulls":29},7,-95.51745777861296,40.1601536140089,9.7530130275377]
[null,"2) All pressures are in inches of water (Pascals)"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[{"$nulls":27}," ",null,null," "]
[{"$nulls":29},"12x6"]
[{"$nulls":29},"34x36"]