{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Velocity range"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Velocity range","index":0,"n_rows":30,"n_cols":40,"rows_kept":30,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[5,1,5,7],[9,1,9,5],[9,7,9,11]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"600 / 600A / 600C / 5600 / 5600A Door Grille"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},16,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null,"Based on Titus T-700 - 50711701.xls"]
[null,"Enter Duct Height in inches =",{"$nulls":6},16,"Inches",{"$nulls":11},1.7777777777777777,1.6150173611111112,0.75]
[null,"Enter Minimum Neck Velocity (greater than 0)=",{"$nulls":6},110,"FPM"]
[null,"Enter Maximum Neck Velocity =",{"$nulls":6},500,"FPM"]
[{"$nulls":26},"Pressure Constants",null,null,null," "]
[{"$nulls":27},"m","b",null," "," "]
[null,"600 / 600A / 600C / 5600 / 5600A Door Grille",{"$nulls":24},"0 Degrees",0,-11.3]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","based on s80 / adjusted to Titus catalog NC values."]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",9.753013027537682,9.753013027537703,9.753013027537708,9.753013027537703,9.753013027537696,9.7530130275377]
[null,null,null,110,177.65190972222223,0.009278663842481544,11.803548334167038,null,null,0.5588000000000001,83.8423568984375,2.3103872967779044,48.916687034138,18.984130914628267,12.593671517042782," - "," - "," - ",{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",-5.334008073245482,30.744139414847908,34.3285351004995,43.53792844512962,39.66120807631725,40.1601536140089]
[null,null,null,158.75,256.3840060763889,0.019325357582048657,19.48714340930193,null,null,0.80645,120.99976506933595,4.8120140379301155,48.06686727356998,23.882319450833222,18.062929733220702," - "," - "," - ",{"$nulls":8},"0 deg",null,-88.72871022823963,48.22711834204125,10,null,"B",57.77513719992817,-45.807085295834995,-59.51470382682234,-93.71293688551766,-88.41143050570288,-95.51745777861296]
[null,null,null,207.5,335.11610243055554,0.03301689835271454,25.096167884362934,null,null,1.0541,158.15717324023439,8.22120768982592,47.4464988405897,27.45799712702238,22.05548828100854," - "," - "," - "]
[null,16,null,256.25,413.84819878472223,0.05035328615447919,29.515979425138916,406.4,null,1.3017500000000002,195.31458141113282,12.537968252465319,46.95765954744513,30.275567549398545,25.20155341679038,13.185653409349316," - "," - "]
[null,"x",1.7777777777777777,305,492.5802951388889,0.07133452098734261,33.16368407375547,"x",0.16516096,1.5494,232.47198958203128,17.76229572584831,46.55421669799803,32.60093021083493,27.798025305867146,16.478686653717787,12.149257244099587," - ",{"$nulls":8}," ",{"$nulls":4},"From S80P Sound Analysis.xls"]
[null,16,null,353.75,571.3123914930555,0.09596060285130478,36.269346965773686,406.4,null,1.79705,269.6293977529297,23.89419010997489,46.210724664712615,34.58074854147928,30.008666564646806,19.28238161654771,14.703304560417394," - ",{"$nulls":13},"Band","Const","Slope 1","Slope 2","NC"]
[null,null,null,402.5,650.0444878472223,0.12423153174636571,38.97341429939012,null,null,2.0447,306.7868059238282,30.93365140484506,45.9116498395113,36.304555104049044,31.93344817232678,21.72352871654303,16.927086135138666,11.120695177133031,{"$nulls":13},2,57.77513719992817,-5.334008073245482,9.753013027537682,10]
[null,null,null,451.25,728.7765842013889,0.15614730767252544,41.367954877259216,null,null,2.2923500000000003,343.9442140947266,38.880679610458834,45.646809243324704,37.831042522152615,33.6379056042213,23.885244778423967,18.896317873856546,13.114700225499549,{"$nulls":13},3,-45.807085295834995,30.744139414847908,9.753013027537703,35.680029057786996," ",null,null," "]
[null,null,null,500,807.5086805555555,0.19170793062978392,43.51660752519674,null,null,2.54,381.101622265625,47.73527472681619,45.409164304860525,39.200779691472306,35.16733759973005,25.824980936323186,20.663335325514907,14.903947092631883,{"$nulls":13},4,-59.51470382682234,34.3285351004995,9.753013027537708,-78.94438574956783]
[{"$nulls":26}," "," ",null,null,null,5,-93.71293688551766,43.53792844512962,9.753013027537703]
[{"$nulls":31},6,-88.41143050570288,39.66120807631725,9.753013027537696,{"$nulls":4}," "]
[null,"1) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991.",{"$nulls":29},7,-95.51745777861296,40.1601536140089,9.7530130275377]
[null,"2) All pressures are in inches of water (Pascals)"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[{"$nulls":27}," ",null,null," "]
[{"$nulls":29},"12x6"]
[{"$nulls":29},"34x36"]