{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["600C"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"600C","index":0,"n_rows":30,"n_cols":40,"rows_kept":30,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[9,1,9,5],[9,7,9,11],[5,2,5,4],[5,8,5,9],[8,1,8,5]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"600 / 600A / 600C / 5600 / 5600A Door Grille"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},16,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null,"Based on Titus T-700 - 50711701.xls"]
[null,"Enter Duct Height in inches =",{"$nulls":6},16,"Inches",{"$nulls":11},1.7777777777777777,1.6150173611111112,0.75]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},399,"CFM"]
[null,"Series =","600C",{"$nulls":4},"Tag =","Room 23"]
[{"$nulls":26},"Pressure Constants",null,null,null," "]
[null,"600C Door Grille",{"$nulls":25},"m","b",null," "," "]
[null,"Tag : Room 23",{"$nulls":24},"0 Degrees",0,-11.3]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","based on s80 / adjusted to Titus catalog NC values."]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",9.753013027537682,9.753013027537703,9.753013027537708,9.753013027537703,9.753013027537696,9.7530130275377]
[null,"16 x 16",1.7777777777777777,247.05616769685568,399,0.04680491613721298,28.750703136772607,"406 x 406",0.16516096,1.255045331900027,188.3070126,11.654424118166032,47.04230051378815,29.787714206523177,24.656822260754016,12.494786000532956," - "," - ",{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",-5.334008073245482,30.744139414847908,34.3285351004995,43.53792844512962,39.66120807631725,40.1601536140089]
[{"$nulls":26},"0 deg",null,-88.72871022823963,48.22711834204125,10,null,"B",57.77513719992817,-45.807085295834995,-59.51470382682234,-93.71293688551766,-88.41143050570288,-95.51745777861296]
[null,"1) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991."]
[null,"2) All pressures are in inches of water (Pascals)"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB.",{"$nulls":24}," ",{"$nulls":4},"From S80P Sound Analysis.xls"]
[{"$nulls":31},"Band","Const","Slope 1","Slope 2","NC"]
[{"$nulls":31},2,57.77513719992817,-5.334008073245482,9.753013027537682,10]
[{"$nulls":31},3,-45.807085295834995,30.744139414847908,9.753013027537703,35.680029057786996," ",null,null," "]
[{"$nulls":31},4,-59.51470382682234,34.3285351004995,9.753013027537708,-78.94438574956783]
[{"$nulls":26}," "," ",null,null,null,5,-93.71293688551766,43.53792844512962,9.753013027537703]
[{"$nulls":31},6,-88.41143050570288,39.66120807631725,9.753013027537696,{"$nulls":4}," "]
[{"$nulls":31},7,-95.51745777861296,40.1601536140089,9.7530130275377]
[]
[]
[{"$nulls":27}," ",null,null," "]
[{"$nulls":29},"12x6"]
[{"$nulls":29},"34x36"]