{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["size"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"size","index":0,"n_rows":24,"n_cols":40,"rows_kept":24,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[9,1,9,5],[9,7,9,11],[5,2,5,4],[5,8,5,9],[8,1,8,5]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"AFCS85(H,V)  1/2\" Spacing 30° Deflection"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},20,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},20,"Inches",{"$nulls":11},2.7777777777777777,2.5733506944444446,0.75,{"$nulls":8},"\"",null,"Based on:","Titus Models 25R Return 1/2\" Spacing 30° Deflection"]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},1222,"CFM",{"$nulls":22}," "]
[null,"Series =","AFCS85 H or V",{"$nulls":4},"Tag =","Room 23"]
[{"$nulls":26},"Pressure Constants",null,null,null," "]
[null,"AFCS85 H or V Return Grille",{"$nulls":25},"m","b",null," "," "]
[null,"Tag : Room 23",{"$nulls":24}," ",0,4.1166741347524285]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","from : ","AFSC85 Sound Regression"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7","NC"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",10.249067640048848,10.457986254944725,10.454102164900009,12.915498125785941,13.383557288081624,11.880865529983597,11.84485318524727]
[null,"20 x 20",2.7777777777777777,474.8672626075223,1222,-0.04381580716544471,22.51980853601733,"508 x 508",0.258064,2.4123256940462134,576.7197228,-10.910135984195733,33.109203103113536,38.19523579500934,38.37595382147592,27.55379631062026,22.69036460451297,18.47180156676111,{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",84.2575152721979,91.08407583797667,96.37125141423752,135.94239595409556,143.87992466327952,132.49015995660827,106.60367866722542]
[{"$nulls":26}," ",null,-267.67493753246436,106.60367866722542,11.84485318524727,null,"B",-196.61935423663496,-209.8908648610479,-223.86005974380444,-341.60764437221036,-367.90858280526925,-341.0247644920162,-267.67493753246436]
[]
[{"$nulls":27}," "]
[{"$nulls":26}," ","Band","Const","Slope 1","Slope 2"]
[{"$nulls":27},2,-196.61935423663496,84.2575152721979,10.249067640048848]
[{"$nulls":27},3,-209.8908648610479,91.08407583797667,10.457986254944725]
[{"$nulls":27},4,-223.86005974380444,96.37125141423752,10.454102164900009,{"$nulls":5}," ",null,null," "]
[{"$nulls":27},5,-341.60764437221036,135.94239595409556,12.915498125785941]
[{"$nulls":26}," ",6,-367.90858280526925,143.87992466327952,13.383557288081624]
[{"$nulls":27},7,-341.0247644920162,132.49015995660827,11.880865529983597,{"$nulls":8}," "]