{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["size"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"size","index":0,"n_rows":24,"n_cols":40,"rows_kept":24,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[9,1,9,5],[9,7,9,11],[5,2,5,4],[5,8,5,9],[8,1,8,5]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"AFS580 (H,V)  Aluminum Return"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},20,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},20,"Inches",{"$nulls":11},2.7777777777777777,2.5733506944444446,0.75,{"$nulls":8},"\"",null,"Based on:","Titus Models 3F Return Aluminum"]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},1222,"CFM",{"$nulls":22}," "]
[null,"Series =","AFS580 H or V",{"$nulls":4},"Tag =","Room 23"]
[{"$nulls":26},"Pressure Constants",null,null,null," "]
[null,"AFS580 H or V Return Grille",{"$nulls":25},"m","b",null," "," "]
[null,"Tag : Room 23",{"$nulls":24}," ",0,7.209854123534171]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","from : ","AFS580 Sound Regression"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7","NC"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",8.97063112627595,9.179549741171828,9.17566565112711,11.637061612013042,12.105120774308723,10.6024290162107,10.566416671474377]
[null,"20 x 20",2.7777777777777777,474.8672626075223,1222,-0.08730132154927009,34.87825362960947,"508 x 508",0.258064,2.4123256940462134,576.7197228,-21.738029065768252,45.46764819670572,50.5536808886015,50.73439891506806,39.91224140421237,35.04880969810516,30.830246660353268,{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",34.02667290200247,40.853233467781244,46.140409044042066,85.71155358390013,93.64908229308406,82.25931758641285,56.37283629703001]
[{"$nulls":26}," ",null,-120.34521776632485,56.37283629703001,10.566416671474377,null,"B",-49.289634470495336,-62.56114509490833,-76.5303399776648,-194.2779246060708,-220.57886303912957,-193.6950447258766,-120.34521776632485]
[]
[{"$nulls":27}," "]
[{"$nulls":26}," ","Band","Const","Slope 1","Slope 2"]
[{"$nulls":27},2,-49.289634470495336,34.02667290200247,8.97063112627595]
[{"$nulls":27},3,-62.56114509490833,40.853233467781244,9.179549741171828]
[{"$nulls":27},4,-76.5303399776648,46.140409044042066,9.17566565112711,{"$nulls":5}," ",null,null," "]
[{"$nulls":27},5,-194.2779246060708,85.71155358390013,11.637061612013042]
[{"$nulls":26}," ",6,-220.57886303912957,93.64908229308406,12.105120774308723]
[{"$nulls":27},7,-193.6950447258766,82.25931758641285,10.6024290162107,{"$nulls":8}," "]