{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["size"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"size","index":0,"n_rows":24,"n_cols":40,"rows_kept":24,"cut":false,"hidden":false,"merged":[[11,12,11,17],[11,6,12,6],[2,1,2,7],[3,1,3,7],[4,1,4,7],[9,1,9,5],[9,7,9,11],[5,2,5,4],[5,8,5,9],[8,1,8,5]],"flags":["formulas_cached_only"]}
[{"$nulls":28},"AFS580Z, 585Z (H,V)  Aluminum Return, Zero Deflection"]
[{"$nulls":8},"Input Data",{"$nulls":12},"Nominal Duct","Core Area","H & W",null,null," "," "]
[null,"Enter Duct Width in inches =",{"$nulls":6},18,"Inches",{"$nulls":11},"Area ( ft2 )","( ft2 )","border",null,null," Free area & Core Area Ratio",null,"Ak/Ac",1,null,null," - ",null," "]
[null,"Enter Duct Height in inches =",{"$nulls":6},18,"Inches",{"$nulls":11},2.25,2.06640625,0.75,{"$nulls":8},"\"",null,"Based on:","Titus Models 55F,56F Return Aluminum"]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},1222,"CFM",{"$nulls":22}," "]
[null,"Series =","AFS580 / AFS585 HZ or VZ",{"$nulls":4},"Tag =","Room 23"]
[{"$nulls":26},"Pressure Constants",null,null,null," "]
[null,"AFS580 / AFS585 HZ or VZ Return Grille",{"$nulls":25},"m","b",null," "," "]
[null,"Tag : Room 23",{"$nulls":24}," ",0,2.3160868549331712]
[null,"IP Data",{"$nulls":5},"Metric Data",{"$nulls":24}," "]
[null,"Nom","Duct ","Neck","Air"," ",null,"Nom","Duct ","Neck","Air"," ",{"$nulls":19}," ","from : ","Titus 13R Data"]
[null,"Duct","Area","Vel","Flow","Ps","Nc","Duct","Area","Vel","Flow","Ps","Octave Band, dB",{"$nulls":20},"2","3","4","5","6","7","NC"]
[null,"in","ft²","FPM","CFM","\"WG",null,"mm","m²","m/s","L/s","Pa",2,3,4,5,6,7,{"$nulls":8},"Sound",{"$nulls":5},"M(An)",10,10,10,10,10,10,10]
[null,"18 x 18",2.25,591.3648393194707,1222,-0.028693961346948137,24.119224164593618,"457 x 457",0.20903184000000002,3.004133383742911,576.7197228,-7.1447963753900865,49.11426554502094,40.20392136684195,29.301827759424015,19.44498617531511,20.65964952059288,14.370766236821794,{"$nulls":10},"B","CVn","CAn",null,"M(Vn)",13.205083000697508,50.503987893846116,100.39731623832925,93.60202780183769,38.953710903304824,76.54845418876445,64.4187228585656]
[{"$nulls":26}," ",null,-157.59232410851325,64.4187228585656,10,null,"B",9.359526545133612,-102.93799227463047,-252.137182426257,-243.15846638914078,-90.4665653275585,-200.96264452751151,-157.59232410851325]
[]
[{"$nulls":27}," "]
[{"$nulls":26}," ","Band","Const","Slope 1","Slope 2"]
[{"$nulls":27},2,9.359526545133612,13.205083000697508,10]
[{"$nulls":27},3,-102.93799227463047,50.503987893846116,10]
[{"$nulls":27},4,-252.137182426257,100.39731623832925,10,{"$nulls":5}," ",null,null," "]
[{"$nulls":27},5,-243.15846638914078,93.60202780183769,10]
[{"$nulls":26}," ",6,-90.4665653275585,38.953710903304824,10]
[{"$nulls":27},7,-200.96264452751151,76.54845418876445,10,{"$nulls":8}," "]