{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["cfm"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"cfm","index":0,"n_rows":62,"n_cols":40,"rows_kept":62,"cut":false,"hidden":false,"merged":[[59,12,59,17],[60,12,60,17],[61,12,61,17],[56,12,56,17],[57,12,57,17],[46,2,46,3],[46,5,46,6],[58,12,58,17],[8,1,8,11],[21,1,21,11],[44,5,44,7],[44,2,44,4],[10,12,10,17],[9,5,9,6],[9,7,11,7],[1,1,1,7],[22,5,22,6],[22,7,24,7],[23,12,23,17],[2,1,2,7],[3,1,3,7],[4,1,4,7]],"flags":["formulas_cached_only"]}
[{"$nulls":26},"Use neck area and velocity for sound on this unit."]
[null,"Enter Duct Width in inches =",{"$nulls":6},20,"Inches",{"$nulls":5}," ",{"$nulls":10},"Ac = ((L-0.75)*(W-0.75)/144)",null,null,"Core Length =",null,19.25,"Mk =",0.4]
[null,"Enter Duct Height in inches =",{"$nulls":6},18,"Inches",{"$nulls":16},"Reduction =",null,0.75,"Core Width =",null,17.25,null,null,null," - "]
[null,"Enter Minimum Air Flow (must be greater than 0)=",{"$nulls":6},520,"CFM",{"$nulls":17},"X","Y","Ak","An/Ac","Ac"]
[null,"Enter Maximum Air Flow =",{"$nulls":6},1500,"CFM",{"$nulls":17},20,18,3.2210708503466834,1.0841332580463015,2.3059895833333335]
[]
[{"$nulls":26},"Throw Zones From T-94 Catalog using Ak = Ac*(Ac)^Mk",{"$nulls":6},"Use neck area for throw on this unit."]
[null,"180 / 5180 / 180M / 5180M Horizontal Supply Data",{"$nulls":25},"c(ii)","c(iii)","c(iv)"]
[null,"IP Data",{"$nulls":24},"1 Way",4,4,20,"From Titus 250",null,"Pressure Constants",null,5.735963566034226,null,"N.C.","B","CVn","CAn"]
[null,"Nom","Duct ","Neck","Air","Pressure",null,"NC","1 Way","2 Way","3 Way ","4 Way",{"$nulls":14},"2 Way",3.5,3.5,19,null,"Core",{"$nulls":5},-131.43627616601188,59.41821349173295,7.100084939221003]
[null,"Duct","Area","Vel","Flow","Pt","Ps",null,"Throw  ","Throw  ","Throw  ","Throw  ","Octave Band, dB",{"$nulls":13},"3 Way ",3,3,17,null,"Vel"]
[null,"in","ft²","FPM","CFM","\"WG","\"WG",null,"ft","ft","ft","ft",2,3,4,5,6,7,{"$nulls":8},"4 Way",2.8,2.8,15,null,"fpm"]
[null,null,null,208,520,0.01818416436187473,0.015013962153905158,10.959773329384769,"9 - 13 - 26","8 - 11 - 23","7 - 10 - 20","6 - 9 - 18",11.959773329384769,16.959773329384767,22.959773329384767,20.959773329384767,15.959773329384769,10.959773329384769,{"$nulls":13},225.4997176736307]
[null,null,null,273.3333333333333,683.3333333333334,0.03140160697352833,0.025927093997282387,18.008512186937047,"11 - 17 - 34","10 - 15 - 30","9 - 13 - 26","8 - 12 - 24",19.008512186937047,24.008512186937047,30.008512186937047,28.008512186937047,23.008512186937047,18.008512186937047,{"$nulls":8},"Square or Rectangular",{"$nulls":4},296.3297571993224]
[null,20,null,338.6666666666667,846.6666666666667,0.048207164199979884,0.03980279348789223,23.539150916629374,"14 - 21 - 42","12 - 19 - 37","11 - 16 - 32","10 - 15 - 30",24.539150916629374,29.539150916629374,35.539150916629374,33.539150916629374,28.539150916629374,23.539150916629374,{"$nulls":8},".5 for Square, .6 for Rectangular",{"$nulls":4},367.15979672501413]
[null,"x",2.5,404.00000000000006,1010.0000000000001,0.06860083604122934,0.05664106062573465,28.091115598225223,"17 - 25 - 51","15 - 22 - 44","13 - 19 - 38","12 - 18 - 35",29.091115598225223,34.09111559822522,40.09111559822522,38.09111559822522,33.09111559822522,28.091115598225223,{"$nulls":9},0.6,null,null,null,437.9898362507058]
[null,18,null,469.3333333333334,1173.3333333333335,0.09258262249727674,0.07644189541080969,31.959243374738143,"20 - 29 - 59","17 - 26 - 51","15 - 22 - 44","14 - 21 - 41",32.95924337473814,37.95924337473814,43.95924337473814,41.95924337473814,36.95924337473814,31.959243374738143,{"$nulls":13},508.81987577639757]
[null,null,null,534.6666666666667,1336.6666666666667,0.12015252356812203,0.0992052978431173,35.322415812537535,"22 - 33 - 67","20 - 29 - 59","17 - 25 - 50","16 - 23 - 47",36.322415812537535,41.322415812537535,47.322415812537535,45.322415812537535,40.322415812537535,35.322415812537535,{"$nulls":13},579.6499153020892]
[null,null,null,600,1500,0.15131053925376528,0.12493126792265752,38.297375312829125,"25 - 38 - 75","22 - 33 - 66","19 - 28 - 56","18 - 26 - 53",39.297375312829125,44.297375312829125,50.297375312829125,48.297375312829125,43.297375312829125,38.297375312829125,{"$nulls":13},650.4799548277808]
[]
[null,"180 / 5180 / 180M / 5180M Horizontal Supply Data"]
[null,"Metric Data"]
[null,"Nom","Duct ","Neck","Air","Pressure",null,"NC","1 Way","2 Way","3 Way ","4 Way"]
[null,"Duct","Area","Vel","Flow","Pt","Ps",null,"Throw  ","Throw  ","Throw  ","Throw  ","Octave Band, dB"]
[null,"mm","m²","m/s","L/s","Pa","Pa",null,"m","m","m","m",2,3,4,5,6,7]
[null,null,null,1.05664,245.41264800000002,4.527856926106808,3.7384765763223844,10.959773329384769,"2.6 - 4.0 - 7.9","2.3 - 3.5 - 6.9","2.0 - 3.0 - 5.9","1.8 - 2.8 - 5.5",11.959773329384769,16.959773329384767,22.959773329384767,20.959773329384767,15.959773329384769,10.959773329384769]
[null,null,null,1.3885333333333334,322.49739000000005,7.819000136408555,6.455846405323315,18.008512186937047,"3.5 - 5.2 - 10.4","3.0 - 4.6 - 9.1","2.6 - 3.9 - 7.8","2.4 - 3.6 - 7.3",19.008512186937047,24.008512186937047,30.008512186937047,28.008512186937047,23.008512186937047,18.008512186937047]
[null,508,null,1.7204266666666668,399.58213200000006,12.00358388579499,9.910895578485166,23.539150916629374,"4.3 - 6.4 - 12.9","3.8 - 5.6 - 11.3","3.2 - 4.8 - 9.7","3.0 - 4.5 - 9.0",24.539150916629374,29.539150916629374,35.539150916629374,33.539150916629374,28.539150916629374,23.539150916629374]
[null,"x",0.2322576,2.0523200000000004,476.66687400000006,17.081608174266105,14.103624095807929,28.091115598225223,"5.1 - 7.7 - 15.4","4.5 - 6.7 - 13.5","3.8 - 5.8 - 11.5","3.6 - 5.4 - 10.8",29.091115598225223,34.09111559822522,40.09111559822522,38.09111559822522,33.09111559822522,28.091115598225223]
[null,457.2,null,2.384213333333334,553.7516160000001,23.053073001821907,19.034031957291614,31.959243374738143,"6.0 - 8.9 - 17.9","5.2 - 7.8 - 15.6","4.5 - 6.7 - 13.4","4.2 - 6.3 - 12.5",32.95924337473814,37.95924337473814,43.95924337473814,41.95924337473814,36.95924337473814,31.959243374738143]
[null,null,null,2.716106666666667,630.836358,29.917978368462386,24.702119162936206,35.322415812537535,"6.8 - 10.2 - 20.4","5.9 - 8.9 - 17.8","5.1 - 7.6 - 15.3","4.8 - 7.1 - 14.3",36.322415812537535,41.322415812537535,47.322415812537535,45.322415812537535,40.322415812537535,35.322415812537535]
[null,null,null,3.048,707.9211,37.67632427418756,31.107885712741723,38.297375312829125,"7.6 - 11.4 - 22.8","6.7 - 10.0 - 20.0","5.7 - 8.6 - 17.1","5.3 - 8.0 - 16.0",39.297375312829125,44.297375312829125,50.297375312829125,48.297375312829125,43.297375312829125,38.297375312829125]
[]
[null,"1) Throw values are given for terminal velocities of 150, 100, and 50 FPM. (0.75, 0.50, and 0.25 m/s)"]
[null,"2) Throw values are given for isothermal conditions."]
[null,"3) NC values are based on octave band 2 - 7 sound power levels minus a room absorption of 10dB, re 1.0 E-12 watts."]
[null,"4) Dash (-) in space denotes a NC or dB value of less than 10."]
[null,"5) Data was obtained in accordance with ANSI/ASHRAE Standard 70-1991, ISO Standard 5219, and ISO Standard 3741."]
[null,"6) The throw values given for 1-Way Throw is for [Total CFM] CFM per side. ([Total L/s] L/s per side)"]
[null,"7) The throw values given for 2-Way Throw is for [Total CFM/2] CFM per side. ([Total L/s / 2] L/s per side)"]
[null,"8) The throw values given for 3-Way Throw is for [Total CFM/3] CFM per side. ([Total L/s / 3] L/s per side)"]
[null,"9) The throw values given for 4-Way Throw is for [Total CFM/4] CFM per side. ([Total L/s / 4] L/s per side)"]
[null,"10) See K-Select program for performance data not shown, including octave band data."]
[null,"Correction Factors"]
[null,null,"With OBD",null,null,"Without OBD"]
[null,"Blade","Throw","Ps","NC","Throw","Ps","NC"]
[null,"Setting","(Multiply)",null,"(Add)","(Multiply)",null,"(Add)"]
[null,"A",1.43,1.3,2,1.43,1.2,0]
[null,"B",1,1,0,1,0.85,-3]
[null,"C",0.79,0.72,-3,0.7,0.61,-4]
[null,"D",0.64,0.52,-4,0.64,0.33,-6]
[]
[]
[]
[]
[]
[{"$nulls":11},"Blade","Drop"]
[{"$nulls":11},"Setting"]
[{"$nulls":11},"A","Pattern stays on ceiling"]
[{"$nulls":11},"B","10% of Throw"]
[{"$nulls":11},"C","20% of Throw"]
[{"$nulls":11},"D","30% of Throw"]