{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["CFM"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"CFM","index":0,"n_rows":59,"n_cols":45,"rows_kept":59,"cut":false,"hidden":false,"merged":[[11,39,11,40],[11,41,11,42],[11,43,11,44],[27,27,27,28],[28,27,28,28],[23,27,23,28],[24,27,24,28],[25,27,25,28],[26,27,26,28],[2,1,2,7],[3,1,3,7],[4,1,4,7],[5,1,5,7],[11,10,12,10],[37,10,38,10],[35,1,35,16],[9,1,9,16],[37,11,37,16],[10,6,10,7],[10,8,10,9],[36,6,36,7],[36,8,36,9],[11,11,11,16]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":8},"Input Data",{"$nulls":11},"Nominal Duct","Core Area","H & W"]
[null,"Enter (Side B) in inches =",{"$nulls":6},9,"Inches",{"$nulls":10},"Area '( ft2 )","( ft2 )","border",null,null," - "]
[null,"Enter (Side A) in inches =",{"$nulls":6},21,"Inches",{"$nulls":10},1.3125,1.3125,0,null,null,"\"",{"$nulls":7},"Throw Zones"]
[null,"Enter Minimum Air Flow (must be greater than 0) =",{"$nulls":6},263,"CFM",{"$nulls":10},"Area created by Side B =",null,0.5625,{"$nulls":11},"c(ii)","c(iii)","c(iv)"]
[null,"Enter Maximum Air Flow =",{"$nulls":6},952,"CFM",{"$nulls":10},"Area created by Side A =",null,3.0625,null,null,"Throw Zones",{"$nulls":6},1,"3L - Side A, (\"A\",LT,\"B\") AND (\"A\",LT,\"2*B\")",4.44,5.07,9.94]
[{"$nulls":26},"c(ii)","c(iii)","c(iv)",{"$nulls":4},"3L - Side B, (\"A\",LT,\"B\") AND (\"A\",LT,\"2*B\")",2.22,4.8,7.83]
[{"$nulls":25},"3L - Side A, (\"A\",GT,\"2*B\")",6,7.6,10.85,null,null,null,2,"3L - Side A, (\"A\",EQ,\"2*B\")",5.51,6.8,10.75]
[null,"5SHV -  No OBD, Rectangular, 3L - Three Way Throw Pattern",{"$nulls":23},"3L - Side B, (\"A\",GT,\"2*B\")",2.22,3.63,7.83,{"$nulls":4},"3L - Side B (\"A\",EQ,\"2*B\")",2.22,3.63,7.83]
[null,"IP Data",{"$nulls":30},3,"3L - Side A, (\"A\",GT,\"2*B\")",6,7.6,10.85]
[null,"Neck","Neck","Total","Total","Static","Pattern 3L Side A",null,"Pattern 3L Side B",{"$nulls":16},"Throw uses total CFM",{"$nulls":7},"3L - Side B, (\"A\",GT,\"2*B\")",2.22,3.63,7.83]
[null,"Dim","Vel","Flow","Pres","Pres","flow","Throw","flow","Throw","NC","Octave Band, dB",{"$nulls":27},"Velocity if 1 is used",null,"Velocity if 2 is used",null,"Velocity if 3 is used"]
[null,"in","FPM","CFM","\"WG","\"WG","CFM","ft","CFM","ft",null,2,3,4,5,6,7,{"$nulls":8},"Pressure Constants",null,null,null," ",null,null,null,"A<B",0,{"$nulls":4},"A","B","A","B","A","B"]
[null,null,200.38095238095238,263,0.018799563644009427,0.016296292852530144,150.28571428571428,"12 - 17 - 25",56.357142857142854,"5 - 8 - 17"," - "," - ",12.092462971269377,18.092462971269377,16.092462971269377,11.092462971269377," - ",{"$nulls":10},"b",null," "," ",null,null,"A<(2*B)",0,{"$nulls":4},153.41666666666666,54.79166666666667,153.41666666666666,54.79166666666667,150.28571428571428,56.357142857142854]
[null,null,266,349.125,0.03312822517421264,0.028717010104410693,199.5,"15 - 20 - 29",74.8125,"7 - 11 - 21",13.502270780478021,14.502270780478021,19.50227078047802,25.50227078047802,23.50227078047802,18.50227078047802,13.502270780478021,{"$nulls":8},"Pressure Constants",null,7.51,{"$nulls":5},"(B/A)=2",0,{"$nulls":4},203.65625,72.734375,203.65625,72.734375,199.5,74.8125]
[null," ",331.6190476190476,435.25,0.05148892582808748,0.044632877115958654,248.71428571428572,"18 - 23 - 32",93.26785714285714,"9 - 14 - 23",19.269764946444916,20.269764946444916,25.269764946444916,31.269764946444916,29.269764946444916,24.269764946444916,19.269764946444916,{"$nulls":16},"A>(2*B)",1,{"$nulls":4},253.89583333333331,90.67708333333334,253.89583333333331,90.67708333333334,248.71428571428572,93.26785714285714]
[null,"9\"",397.23809523809524,521.375,0.07388166560563399,0.06404389388717407,297.92857142857144,"20 - 25 - 35",111.72321428571429,"11 - 17 - 25",23.99248495762091,24.99248495762091,29.99248495762091,35.99248495762091,33.99248495762091,28.99248495762091,23.99248495762091,{"$nulls":22},304.1354166666667,108.61979166666666,304.1354166666667,108.61979166666666,297.92857142857144,111.72321428571429]
[null,"x",462.85714285714283,607.5,0.1003064445068521,0.08695006041805688,347.14285714285717,"22 - 27 - 38",130.17857142857142,"13 - 19 - 27",27.991520820874392,28.991520820874392,33.99152082087439,39.99152082087439,37.99152082087439,32.99152082087439,27.991520820874392,{"$nulls":16},"Use 1 ",0,{"$nulls":4},354.375,126.5625,354.375,126.5625,347.14285714285717,130.17857142857142]
[null,"21\"",528.4761904761905,693.625,0.13076326253174186,0.11335137670860712,396.35714285714283,"23 - 29 - 40",148.63392857142858,"15 - 21 - 29",31.459471198763673,32.45947119876367,37.45947119876367,43.45947119876367,41.45947119876367,36.45947119876367,31.459471198763673,{"$nulls":8},"Sound",{"$nulls":7},"Use 2 ",0,{"$nulls":4},404.6145833333333,144.50520833333334,404.6145833333333,144.50520833333334,396.35714285714283,148.63392857142858]
[null," ",594.0952380952381,779.75,0.16525211968030326,0.1432478427588248,445.57142857142856,"25 - 30 - 43",167.08928571428572,"16 - 22 - 31",34.52100098367085,35.52100098367085,40.52100098367085,46.52100098367085,44.52100098367085,39.52100098367085,34.52100098367085,{"$nulls":10},"B","CVn","CAn",null,null,null,"Use 3 ",1,{"$nulls":4},454.85416666666663,162.44791666666669,454.85416666666663,162.44791666666669,445.57142857142856,167.08928571428572]
[null,null,659.7142857142857,865.875,0.20377301595253627,0.17663945856870988,494.78571428571433,"26 - 32 - 45",185.54464285714283,"18 - 23 - 33",37.26145497457329,38.26145497457329,43.26145497457329,49.26145497457329,47.26145497457329,42.26145497457329,37.26145497457329,{"$nulls":8},"3L",null,-133.44,60.23,7.55,{"$nulls":9},505.09374999999994,180.39062500000003,505.09374999999994,180.39062500000003,494.78571428571433,185.54464285714283]
[null,null,725.3333333333334,952,0.24632595134844104,0.21352622413826247,544,"27 - 33 - 47",204,"20 - 24 - 34",39.74183164092812,40.74183164092812,45.74183164092812,51.74183164092812,49.74183164092812,44.74183164092812,39.74183164092812,{"$nulls":22},555.3333333333334,198.33333333333331,555.3333333333334,198.33333333333331,544,204]
[null,"1) Throw values are given for terminal velocities of 150, 100, and 50 fpm."]
[null,"2) Throw Values are given for Isothermal Conditions at the listed CFM per side, not total CFM.",{"$nulls":23},"Rectangular Neck Validation:",null,"1=True, 0=False"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB.",{"$nulls":23},"Height = Width?",null,0]
[null,"4) Dash (-) in space denotes an NC or dB value of less than 10.",{"$nulls":23},"Height or Width greater than 36",null,0]
[null,"5) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991.",{"$nulls":23},"Height or Width less than 6",null,0]
[{"$nulls":25},"3\" increments?",null,0]
[null," ",{"$nulls":23},"INVALID",null,0]
[null," ",{"$nulls":23},"SIZE"]
[null," "]
[null," ",{"$nulls":23},"Invalid Neck Size :"]
[null," ",{"$nulls":23},"Height can not equal Width."]
[{"$nulls":25},"Height or Width can not be greater than 36\"."]
[null,"5SHV -  No OBD, Rectangular, 3L - Three Way Throw Pattern",{"$nulls":23},"Height or Width can not be less than 6\"."]
[null,"Metric Data",{"$nulls":23},"Neck must be in 3\" increments."]
[null,"Neck","Neck","Total","Total","Static","Pattern 3L Side A",null,"Pattern 3L Side B"]
[null,"Dim","Vel","Flow","Pres","Pres","flow","Throw","flow","Throw","NC","Octave Band, dB"]
[null,"mm","m/s","L/s","Pa","Pa","L/s","m","L/s","m",null,2,3,4,5,6,7]
[null,null,1.0179352380952382,124.12216620000001,4.681091347358348,4.057776920280006,70.92695211428571,"3.5 - 5.3 - 7.6",26.597607042857142,"1.4 - 2.5 - 5.1"," - "," - ",12.092462971269377,18.092462971269377,16.092462971269377,11.092462971269377," - "]
[null,null,1.35128,164.768636025,8.248928068378948,7.150535515998262,94.1535063,"4.7 - 6.2 - 8.7",35.3075648625,"2.2 - 3.4 - 6.3",13.502270780478021,14.502270780478021,19.50227078047802,25.50227078047802,23.50227078047802,18.50227078047802,13.502270780478021]
[null," ",1.6846247619047618,205.41510585,12.820742531193781,11.113586401873706,117.3800604857143,"5.6 - 6.9 - 9.7",44.017522682142854,"2.8 - 4.2 - 7.0",19.269764946444916,20.269764946444916,25.269764946444916,31.269764946444916,29.269764946444916,24.269764946444916,19.269764946444916]
[null,228.6,2.017969523809524,246.061575675,18.396534735802863,15.946929577906344,140.6066146714286,"6.1 - 7.5 - 10.7",52.72748050178572,"3.3 - 5.0 - 7.7",23.99248495762091,24.99248495762091,29.99248495762091,35.99248495762091,33.99248495762091,28.99248495762091,23.99248495762091]
[null,"x",2.351314285714286,286.7080455,24.976304682206173,21.65056504409616,163.83316885714288,"6.6 - 8.1 - 11.5",61.437438321428566,"3.9 - 5.9 - 8.3",27.991520820874392,28.991520820874392,33.99152082087439,39.99152082087439,37.99152082087439,32.99152082087439,27.991520820874392]
[null,533.4,2.6846590476190477,327.354515325,32.560052370403724,28.224492800443173,187.05972304285714,"7.1 - 8.7 - 12.3",70.14739614107144,"4.5 - 6.3 - 8.9",31.459471198763673,32.45947119876367,37.45947119876367,43.45947119876367,41.45947119876367,36.45947119876367,31.459471198763673]
[null," ",3.0180038095238095,368.00098515,41.14777780039551,35.66871284694737,210.28627722857144,"7.5 - 9.2 - 13.0",78.85735396071429,"5.0 - 6.6 - 9.4",34.52100098367085,35.52100098367085,40.52100098367085,46.52100098367085,44.52100098367085,39.52100098367085,34.52100098367085]
[null,null,3.3513485714285713,408.647454975,50.73948097218153,43.98322518360876,233.51283141428576,"7.9 - 9.7 - 13.7",87.56731178035713,"5.6 - 7.0 - 9.9",37.26145497457329,38.26145497457329,43.26145497457329,49.26145497457329,47.26145497457329,42.26145497457329,37.26145497457329]
[null,null,3.6846933333333336,449.2939248,61.33516188576182,53.168029810427356,256.7393856,"8.3 - 10.2 - 14.4",96.2772696,"6.0 - 7.3 - 10.4",39.74183164092812,40.74183164092812,45.74183164092812,51.74183164092812,49.74183164092812,44.74183164092812,39.74183164092812]
[null,"1) Throw values are given for terminal velocities of 0.75, 0.5 and 0.25 m/s."]
[null,"2) Throw Values are given for Isothermal Conditions at the listed CFM per side, not total CFM."]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[null,"4) Dash (-) in space denotes an NC or dB value of less than 10."]
[null,"5) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991."]
[]
[null," "]
[null," "]
[null," "]
[null," "]
[null," "]