{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Size"],"not_rendered":{"charts":0,"images":4,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Size","index":0,"n_rows":49,"n_cols":31,"rows_kept":49,"cut":false,"hidden":false,"merged":[[5,7,5,9],[5,1,5,6],[14,13,16,13],[14,14,16,14],[14,9,16,9],[14,10,16,10],[14,11,16,11],[14,12,16,12],[35,14,37,14],[35,15,37,15],[35,16,37,16],[33,11,33,16],[35,11,37,11],[35,12,37,12],[35,13,37,13],[30,1,30,16],[14,15,16,15],[14,16,16,16],[14,2,16,2],[14,3,16,3],[14,4,16,4],[14,5,16,5],[14,7,16,7],[14,8,16,8],[35,10,37,10],[32,6,32,7],[32,8,32,9],[33,10,34,10],[35,6,37,6],[35,7,37,7],[35,8,37,8],[35,9,37,9],[35,2,37,2],[35,3,37,3],[35,4,37,4],[35,5,37,5],[2,1,2,7],[3,1,3,7],[4,1,4,7],[28,27,28,28],[12,10,13,10],[9,1,9,16],[11,6,11,7],[11,8,11,9],[12,11,12,16],[14,6,16,6],[29,27,29,28],[24,27,24,28],[25,27,25,28],[26,27,26,28],[27,27,27,28]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":8},"Input Data",{"$nulls":11},"Nominal Duct","Core Area","H & W"]
[null,"Enter Duct Width in inches =",{"$nulls":6},6,"Inches",{"$nulls":10},"Area '( ft2 )","( ft2 )","border",null,null," - "]
[null,"Enter Duct Height in inches =",{"$nulls":6},9,"Inches",{"$nulls":10},0.375,0.375,0,null,null,"\""]
[null,"Enter Air Flow (must be greater than 0) =",{"$nulls":6},396,"CFM"]
[null,"Tag = ",{"$nulls":5},"Test Room",{"$nulls":17},"Throw Zones"]
[{"$nulls":26},"c(ii)","c(iii)","c(iv)"]
[{"$nulls":25},"1S",8.04,10.03,12.16]
[null,"5SH /SH -  No OBD, Rectangular, 1S and 1L - One Way Throw Patterns",{"$nulls":23},"1L",8.04,10.03,12.16]
[null,"IP Data"]
[null,"Tag : Test Room"]
[null,"Neck","Neck","Total","Total","Static","Pattern 1S",null,"Pattern 1L"]
[null,"Dim","Vel","Flow","Pres","Pres","flow","Throw","flow","Throw","NC","Octave Band, dB"]
[null,"in","FPM","CFM","\"WG","\"WG","CFM","ft","CFM","ft",null,2,3,4,5,6,7,{"$nulls":8},"Pressure Constants",null,null,null," "]
[null," ",1056,396,0.4281309109680316,0.35860882481168205,396,"20 - 24 - 34",396,"20 - 24 - 34",35.45921386439736,36.45921386439736,41.45921386439736,47.45921386439736,45.45921386439736,40.45921386439736,35.45921386439736,{"$nulls":10},"b",null," "," "]
[null,"6\" x 9\"",{"$nulls":23},"Pressure Constants",null,6.1582]
[null," "]
[null,"1) Throw values are given for terminal velocities of 150, 100, and 50 fpm."]
[null,"2) Throw Values are given for Isothermal Conditions"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB.",{"$nulls":23},"Sound"]
[null,"4) Dash (-) in space denotes an NC or dB value of less than 10.",{"$nulls":25},"B","CVn","CAn"]
[null,"5) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991.",{"$nulls":23},"1S, 1L",null,-143.44,60.23,7.55]
[]
[null," "]
[null," ",{"$nulls":23},"Rectangular Neck Validation:",null,"1=True, 0=False"]
[null," ",{"$nulls":23},"Height = Width?",null,0]
[null," ",{"$nulls":23},"Height or Width greater than 48",null,0]
[null," ",{"$nulls":23},"Height or Width less than 6",null,0]
[{"$nulls":25},"3\" increments?",null,0]
[null,"5SH /SH -  No OBD, Rectangular, 1S and 1L - One Way Throw Patterns",{"$nulls":23},"INVALID",null,0]
[null,"Metric Data",{"$nulls":23},"SIZE"]
[null,"Tag : Test Room",{"$nulls":23},"Invalid Neck Size :"]
[null,"Neck","Neck","Total","Total","Static","Pattern 1S",null,"Pattern 1L",{"$nulls":16},"Height can not equal Width."]
[null,"Dim","Vel","Flow","Pres","Pres","flow","Throw","flow","Throw","NC","Octave Band, dB",{"$nulls":13},"Height or Width can not be greater than 48\"."]
[null,"mm","m/s","L/s","Pa","Pa","L/s","m","L/s","m",null,2,3,4,5,6,7,{"$nulls":8},"Height or Width can not be less than 6\"."]
[null," ",5.36448,186.8911704,106.60459683103986,89.29359737810883,186.8911704,"6.0 - 7.4 - 10.4",186.8911704,"6.0 - 7.4 - 10.4",35.45921386439736,36.45921386439736,41.45921386439736,47.45921386439736,45.45921386439736,40.45921386439736,35.45921386439736,{"$nulls":8},"Neck must be in 3\" increments."]
[null,"152 x 229"]
[null," "]
[null,"1) Throw values are given for terminal velocities of 0.75, 0.5 and 0.25 m/s."]
[null,"2) Throw Values are given for Isothermal Conditions"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[null,"4) Dash (-) in space denotes an NC or dB value of less than 10."]
[null,"5) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991."]
[]
[null," "]
[null," "]
[null," "]
[null," "]
[null," "]