{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Velocity"],"not_rendered":{"charts":0,"images":4,"macros":1,"external_links":1,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Velocity","index":0,"n_rows":59,"n_cols":31,"rows_kept":59,"cut":false,"hidden":false,"merged":[[27,27,27,28],[28,27,28,28],[23,27,23,28],[24,27,24,28],[25,27,25,28],[26,27,26,28],[2,1,2,7],[3,1,3,7],[4,1,4,7],[5,1,5,7],[11,10,12,10],[37,10,38,10],[35,1,35,16],[9,1,9,16],[37,11,37,16],[10,6,10,7],[10,8,10,9],[36,6,36,7],[36,8,36,9],[11,11,11,16]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":8},"Input Data",{"$nulls":11},"Nominal Duct","Core Area","H & W"]
[null,"Enter (Side A) in inches =",{"$nulls":6},9,"Inches",{"$nulls":10},"Area '( ft2 )","( ft2 )","border",null,null," - "]
[null,"Enter (Side B) in inches =",{"$nulls":6},24,"Inches",{"$nulls":10},1.5,1.5,0,null,null,"\""]
[null,"Enter Minimum Neck Velocity (greater than 0)=",{"$nulls":6},175,"FPM",{"$nulls":10},"Area created by Side A =",null,0.5625]
[null,"Enter Maximum Neck Velocity =",{"$nulls":6},725,"FPM",{"$nulls":15},"Throw Zones"]
[{"$nulls":26},"c(ii)","c(iii)","c(iv)"]
[{"$nulls":25},"D2LR,L A",2.22,3.63,7.83]
[null,"5SHV -  No OBD, Rectangular, D2LL and D2LR - Two Way Throw Patterns",{"$nulls":23},"D2LR,L B",5.08,6,9.49]
[null,"IP Data",{"$nulls":23},"Use 1/2 the square neck area size caused by side A for CFM calculation."]
[null,"Neck","Neck","Total","Total","Static","Pattern D2LL & D2LR Side A",null,"Pattern D2LL & D2LR Side B"]
[null,"Dim","Vel","Flow","Pres","Pres","flow","Throw","flow","Throw","NC","Octave Band, dB"]
[null,"in","FPM","CFM","\"WG","\"WG","CFM","ft","CFM","ft",null,2,3,4,5,6,7,{"$nulls":8},"Pressure Constants",null,null,null," "]
[null,null,175,262.5,0.01433874012041752,0.012429453819429835,49.21875,"0 - 0 - 1",213.28125,"6 - 10 - 20"," - "," - "," - ",14.987670678245912,12.987670678245912," - "," - ",{"$nulls":10},"b",null," "," "]
[null,null,243.75,365.625,0.027817887401983477,0.02411377456550099,68.5546875,"0 - 1 - 2",297.0703125,"10 - 15 - 23",11.655163731710083,12.655163731710083,17.655163731710083,23.655163731710083,21.655163731710083,16.655163731710083,11.655163731710083,{"$nulls":8},"Pressure Constants",null,7.51]
[null," ",312.5,468.75,0.0457230233431681,0.03963473794461043,87.890625,"0 - 1 - 4",380.859375,"12 - 19 - 26",18.15430581166246,19.15430581166246,24.15430581166246,30.15430581166246,28.15430581166246,23.15430581166246,18.15430581166246]
[null,"9\"",381.25,571.875,0.06805414794397141,0.058992343956758175,107.2265625,"1 - 1 - 6",464.6484375,"15 - 20 - 29",23.35575841320253,24.35575841320253,29.35575841320253,35.35575841320253,33.35575841320253,28.35575841320253,23.35575841320253]
[null,"x",450,675,0.09481126120439337,0.08218659260194419,126.5625,"1 - 2 - 8",548.4375,"18 - 22 - 31",27.692478710559335,28.692478710559335,33.692478710559335,39.692478710559335,37.692478710559335,32.692478710559335,27.692478710559335]
[null,"24\"",518.75,778.125,0.12599436312443404,0.10921748388016853,145.8984375,"1 - 3 - 9",632.2265625,"19 - 24 - 34",31.411415954314982,32.41141595431498,37.41141595431498,43.41141595431498,41.41141595431498,36.41141595431498,31.411415954314982,{"$nulls":8},"Sound"]
[null," ",587.5,881.25,0.16160345370409335,0.14008501779143112,165.234375,"1 - 3 - 10",716.015625,"21 - 25 - 36",34.666833072813894,35.666833072813894,40.666833072813894,46.666833072813894,44.666833072813894,39.666833072813894,34.666833072813894,{"$nulls":10},"B","CVn","CAn"]
[null,null,656.25,984.375,0.20163853294337136,0.17478919433573203,184.5703125,"2 - 4 - 11",799.8046875,"22 - 27 - 38",37.56157393348639,38.56157393348639,43.56157393348639,49.56157393348639,47.56157393348639,42.56157393348639,37.56157393348639,{"$nulls":8},"D2LR, D2LL",null,-133.44,60.23,7.55]
[null,null,725,1087.5,0.246099600842268,0.2133300135130712,203.90625,"2 - 5 - 12",883.59375,"23 - 28 - 40",40.16764714164132,41.16764714164132,46.16764714164132,52.16764714164132,50.16764714164132,45.16764714164132,40.16764714164132]
[null,"1) Throw values are given for terminal velocities of 150, 100, and 50 fpm."]
[null,"2) Throw Values are given for Isothermal Conditions at the listed CFM per side, not total CFM.",{"$nulls":23},"Rectangular Neck Validation:",null,"1=True, 0=False"]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB.",{"$nulls":23},"Height = Width?",null,0]
[null,"4) Dash (-) in space denotes an NC or dB value of less than 10.",{"$nulls":23},"Height or Width greater than 36",null,0]
[null,"5) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991.",{"$nulls":23},"Height or Width less than 6",null,0]
[{"$nulls":25},"3\" increments?",null,0]
[null," ",{"$nulls":23},"INVALID",null,0]
[null," ",{"$nulls":23},"SIZE"]
[null," "]
[null," ",{"$nulls":23},"Invalid Neck Size :"]
[null," ",{"$nulls":23},"Height can not equal Width."]
[{"$nulls":25},"Height or Width can not be greater than 36\"."]
[null,"5SHV -  No OBD, Rectangular, D2LL and D2LR - Two Way Throw Patterns",{"$nulls":23},"Height or Width can not be less than 6\"."]
[null,"Metric Data",{"$nulls":23},"Neck must be in 3\" increments."]
[null,"Neck","Neck","Total","Total","Static","Pattern D2LL & D2LR Side A",null,"Pattern D2LL & D2LR Side B"]
[null,"Dim","Vel","Flow","Pres","Pres","flow","Throw","flow","Throw","NC","Octave Band, dB"]
[null,"mm","m/s","L/s","Pa","Pa","L/s","m","L/s","m",null,2,3,4,5,6,7]
[null,null,0.889,123.8861925,3.5703462899839624,3.094934001038029,23.228661093750002,"0.0 - 0.1 - 0.4",100.65753140625,"1.7 - 3.2 - 6.0"," - "," - "," - ",14.987670678245912,12.987670678245912," - "," - "]
[null,null,1.23825,172.55576812500001,6.9266539630938855,6.004329866809747,32.354206523437504,"0.1 - 0.2 - 0.7",140.2015616015625,"2.9 - 4.4 - 7.0",11.655163731710083,12.655163731710083,17.655163731710083,23.655163731710083,21.655163731710083,16.655163731710083,11.655163731710083]
[null," ",1.5875000000000001,221.22534375,11.385032812448857,9.869049748207997,41.479751953125,"0.1 - 0.3 - 1.1",179.745591796875,"3.8 - 5.6 - 8.0",18.15430581166246,19.15430581166246,24.15430581166246,30.15430581166246,28.15430581166246,23.15430581166246,18.15430581166246]
[null,228.6,1.9367500000000002,269.89491937500003,16.945482838048882,14.689093645232786,50.6052973828125,"0.2 - 0.4 - 1.7",219.2896219921875,"4.6 - 6.2 - 8.8",23.35575841320253,24.35575841320253,29.35575841320253,35.35575841320253,33.35575841320253,28.35575841320253,23.35575841320253]
[null,"x",2.286,318.564495,23.60800403989395,20.464461557884103,59.7308428125,"0.3 - 0.6 - 2.3",258.83365218750004,"5.4 - 6.8 - 9.6",27.692478710559335,28.692478710559335,33.692478710559335,39.692478710559335,37.692478710559335,32.692478710559335,27.692478710559335]
[null,609.5999999999999,2.63525,367.234070625,31.372596417984077,27.195153486161963,68.8563882421875,"0.3 - 0.8 - 2.6",298.3776823828125,"5.9 - 7.3 - 10.3",31.411415954314982,32.41141595431498,37.41141595431498,43.41141595431498,41.41141595431498,36.41141595431498,31.411415954314982]
[null," ",2.9845,415.90364625,40.239259972319246,34.88116943006635,77.981933671875,"0.4 - 1.0 - 3.0",337.92171257812504,"6.3 - 7.7 - 10.9",34.666833072813894,35.666833072813894,40.666833072813894,46.666833072813894,44.666833072813894,39.666833072813894,34.666833072813894]
[null,null,3.33375,464.573221875,50.20799470289947,43.522509389597275,87.1074791015625,"0.6 - 1.3 - 3.3",377.4657427734375,"6.7 - 8.2 - 11.5",37.56157393348639,38.56157393348639,43.56157393348639,49.56157393348639,47.56157393348639,42.56157393348639,37.56157393348639]
[null,null,3.6830000000000003,513.2427975,61.27880060972473,53.11917336475473,96.23302453125001,"0.7 - 1.5 - 3.7",417.00977296875004,"7.0 - 8.6 - 12.1",40.16764714164132,41.16764714164132,46.16764714164132,52.16764714164132,50.16764714164132,45.16764714164132,40.16764714164132]
[null,"1) Throw values are given for terminal velocities of 0.75, 0.5 and 0.25 m/s."]
[null,"2) Throw Values are given for Isothermal Conditions at the listed CFM per side, not total CFM."]
[null,"3) N.C. values are based on Octave Band 2 - 7 sound power levels minus a room absorption of 10dB."]
[null,"4) Dash (-) in space denotes an NC or dB value of less than 10."]
[null,"5) Data were obtained from test conducted in accordance with ANSI / ASHRAE Standard 70-1991."]
[]
[null," "]
[null," "]
[null," "]
[null," "]
[null," "]