Guide Specifications:

ByPass Terminal Unit
HVAC Guide Specifications
Size Range: 90 to 4800 Nominal CFM
Krueger Model Number: KLB

Part 1- General

1.01	DELIVERY AND STORAGE:
Units shall be stored and handled per manufacturer’s recommendations.

1.02 QUALITY ASSURANCE:
A.	Insulation shall meet NFPA-90A requirements for flame spread and smoke generation and UL-181 requirements for anti-erosion, corrosion and fungus properties.

1.03 DELIVERY AND STORAGE:
Units shall be stored and handled per manufacturer's recommendations.

Part 2 – Products

2.01 Equipment

A.	General:
Factory-assembled, externally powered, bypass terminal. Unit shall be complete with a damper assembly, externally mounted volume controller, collars for duct connection and all required features. 

B.	Unit Cabinet:
1.	Constructed of 20-gage galvanized steel with round inlet, bypass and discharge collars. All primary air inlet and discharge collars shall accommodate standard flex duct sizes.
2.	Insulated with ½ in. thick, 1.5-lb. equivalent density mat-faced insulation that meets the requirements of UL181 and NFPA-90A.

C.	Damper Assembly:
The control air damper assembly shall be constructed of heavy gauge galvanized steel with solid shaft rotating in Delrin® bearings. Damper shaft shall be marked on the end to indicate damper position. Damper blade shall operate over a full 90°.

D.	Controls:
Units shall have pressure dependent pneumatic or electronic controls, as specified.