## Discharge Calculator
Discharge Calculations per AHRI 885-08
Project / Zone: | Zone ID |  | Octave Band | 2 | 3 | 4 | 5 | 6 | 7 | Comments
Input Parameters: |  | Type | Mid Frequency, Hz | 125 | 250 | 500 | 1000 | 2000 | 4000
Duct Width, in. | 8 |  | Input Pwl | 65 | 63 | 66 | 66 | 66 | 64 | User input, Sound Power rating, From catalog or software
Duct Height, in. | 8 |  | Lining Reduction | 2 | 5.8 | 11.6 | 24.9 | 29 | 17.9 | Calculated | dB/ft = 10^C1 * p/a^C2 * t^C3, not to exceed 40db/band
Lining Thickness, in. | 1 |  | Elbow reduction | 0 | 0 | 0 | 0 | 0 | 0 | From Tables | p/a | 6 | p/a = 2*(Width+Height)/(Width*Height)*12, in inches
Length Lined duct,Ft | 5 |  | Tee Reduction | 0 | 0 | 0 | 0 | 0 | 0 | From Tables,
Number of Elbows | 0 |  | Power splits | 0 | 0 | 0 | 0 | 0 | 0 | Power division | 10 log N
Type | 1 | 1, Lined Rectangular | End Reflection | 10 | 5 | 2 | 1 | 0.15138 | 0.038342 | End Reflection | ERL = 10*Log(1+(a1*c0/Pi*f*(D/12))^a2 )
Number of Tees | 0 |  | Flex Duct Reduction | 5 | 10 | 18 | 19 | 21 | 12 | Typical Flex duct | IL, by Band = (C1+C2*Dia+C3*Dia^2) + ((C4+C5*Dia+C6*Dia^2)*Length)
Type | 1 | 1, Lined Rectangular | Other (Custom) | [6 empty] | Optional User Input
Number of Zones fed | 1 |  | Environmental Adjustment Factor | 2 | 1 | 0 | 0 | 0 | 0 | From AHRI 885-08, | Should always be used
End Reflection, Eq Dia., in. | 8 |  | Room Attenuation | 5.1815 | 6.0846 | 6.9877 | 7.9 | 8.7938 | 9.6969 | Shultz Equation | - 10 * Log(Distance)- 5 * Log(Volume) - 3 * Log(Freq[I]) +25
Flex Length, ft. | 5 |  | Total Attenuation | 24.2 | 27.9 | 38.6 | 52.8 | 58.9 | 39.6 | Arithmetic sum of above factors (Note: Data in ARI 885 is rounded, this is not!)
Diameter, in. | 8 |  | Output Spl | 40.8 | 35.1 | 27.4 | 13.2 | 7.1 | 24.4 | Predicted Room DischargeSound Pressure level
Room Volume, CuFt | 2400 |  | Output NC | 2: 27.012 | Predicted Discharge NC
Distance, ft. | 5 |  | Output RC | 2: 15.9 | Predicted Discharge RC
Note: the results agree with Standard 885 within 1 dB and the differences are due to rounding.
Rectangular conversion
[11 empty] | Height | 15
[11 empty] | Width | 15
[11 empty] | Eq. Diam. | 16.9257

## Radiated Calculator
Radiated Calculations per AHRI 885-08
Project / Zone: | Zone ID
Input Parameters: | [7 empty] | From Discharge sheet
ARI 885-08 |  | Type
Ceiling Type | 1 | 1, Mineral Fiber |  |  |  |  | User inputs only in unshaded areas.
For no ceiling, use discharge calculations
Octave Band | 2 | 3 | 4 | 5 | 6 | 7
Mid Frequency, Hz | 125 | 250 | 500 | 1000 | 2000 | 4000
Input Pwl | 56 | 57 | 58 | 60 | 63 | 55 | User input, Sound Power rating, From catalog or software
Ceiling Plenum / Room Attenuation | 16 | 18 | 20 | 26 | 31 | 36 | From AHRI 885-08
Other (Custom) | 0 | 0 | 0 | 0 | 0 | 0 | User Input
Environmental Adjustment Factor | 2 | 1 | 0 | 0 | 0 | 0 | From AHRI 885-08
Total Attenuation | 18 | 19 | 20 | 26 | 31 | 36 | Arithmetic Sum of Attenuation factors
Output Spl, AHRI 885-08 | 38 | 38 | 38 | 34 | 32 | 19 | Predicted Room RadiatedSound Pressure level
Output NC | 33 | [5 empty] | Predicted Radiated NC
Output RC | 34.6667 | [5 empty] | Predicted Radiated RC

## Room Sound Calculator
Room Sound Calculations
This page adds the sound from the VAV box in the previous examples
to the sound from a selected diffuser
Project | Zone ID
Octave Band | 2 | 3 | 4 | 5 | 6 | 7 |  | Comments:
Mid Frequency, Hz | 125 | 250 | 500 | 1000 | 2000 | 4000
VAV Box Discharge Sound Pressure | 40.8 | 35.1 | 27.4 | 13.2 | 7.1 | 24.4 | Copied from Discharge Tab | From Discharge Sheet
VAV Box Radiated Sound Pressure | 38 | 38 | 38 | 34 | 32 | 19 | Copied from Radiated Tab | From Radiated Sheet
Diffuser Sound Power | 44 | 44.8815 | 43.5934 | 46.2168 | 43.5235 | 26.7183 | Input this from diffuser manufacturer raw (uncorrected) sound power data | User input, Sound Power (PWL) rating, from catalog or software
# of Diffusers | 1 | [5 empty] | Input number of diffuser near observer (within 15 ft.) * | This does not use the Ceiling Array equation from the ASHRAE Applications Handbook.
Room Attenuation | 5.1815 | 6.0846 | 6.9877 | 7.9 | 8.7938 | 9.6969 | From Discharge Sheet | Room Absorption, from Discharge Sound Sheet
Other (Custom) | 0 | 0 | 0 | 0 | 0 | 0 | User defined attenuation | Optional User Input
Environmental Adjustment Factor | 2 | 1 | 0 | 0 | 0 | 0 | From ARI 885-98 | From ARI 885-98, Should always be used
Diffuser Sound Pressure | 36.8185 | 37.7969 | 36.6058 | 38.3168 | 34.7296 | 17.0214 | Resultant room sound pressure from diffuser(s) | Diffuser Sound Power less attenuation factors
Total Room Sound Pressure | 43.6434 | 41.922 | 40.5828 | 39.6941 | 36.591 | 26.0769 | Log sum of Discharge, Radiated and diffuser sound pressure levels. | Log add Diffuser, Dischg and Rad sound pressures. db=10*log((10^(Disch/10)+(10^(Rad/10))+10^(Diff/10)))
Output NC | 38.288 | [5 empty] | Predicted Room NC | Calculated NC
|  | R? | H?
Output RC, Letters | 38.956 | N | N |  |  |  | Predicted Room RC | RC can have an "H" or an "R" designation (Hiss or Rumble). N = Neutral.
DbA | 43.8082 | [5 empty] | Predicted Room dBA | DbA based on 125-4000 Hz band data, be sure to consider other low freq. sources

## DbA Calc
Linear, dBA, and dBC Calculations:
June 15, 1995 Version |  |  |  |  | Input O.B. Data Given
Data | Linear | dBA | dBC | No. | Under Linear Column
Freq., Hz. | Input | Calc. | Calc. | Freq., Hz.
31.5 | 79 | 39.6 | 76 | 31.5 | Excluded, DIH 10/15/03
63 | 74 | 47.8 | 73.2 | 63
125 | 43.6434 | 27.5434 | 43.4434 | 125
250 | 41.922 | 33.322 | 41.922 | 250
500 | 40.5828 | 37.3828 | 40.5828 | 500
1000 | 39.6941 | 39.6941 | 39.6941 | 1000
2000 | 36.591 | 37.791 | 36.391 | 2000
4000 | 26.0769 | 27.0769 | 25.2769 | 4000
8000 | 36 | 34.9 | 33 | 8000 | Excluded, DIH 10/15/03
16000 |  | -6.6 | -8.5 | 16000
Linear | 80.1962 | - | - | Linear
dBA | - | 43.8082 | - | dBA
dBC | - | - | 77.8368 | dBC
A-wgt | Linear | dBA | dBC | C-wgt
-39.4 | 79 | 39.6 | 76 | -3 | Excluded, DIH 10/15/03
-26.2 | 74 | 47.8 | 73.2 | -0.8
-16.1 | 43.6434 | 27.5434 | 43.4434 | -0.2
-8.6 | 41.922 | 33.322 | 41.922 | 0
-3.2 | 40.5828 | 37.3828 | 40.5828 | 0
0 | 39.6941 | 39.6941 | 39.6941 | 0
1.2 | 36.591 | 37.791 | 36.391 | -0.2
1 | 26.0769 | 27.0769 | 25.2769 | -0.8
-1.1 | 36 | 34.9 | 33 | -3 | Excluded, DIH 10/15/03
-6.6 | 0 | -6.6 | -8.5 | -8.5
Overall | 80.1962 | 43.8082 | 77.8368 | Overall
Value | Linear | dBA | dBC | Value

## Constants
Sound Constants - ARI 885-08
| Band Constants | [6 empty] | Equation
Octave Band | 2 | 3 | 4 | 5 | 6 | 7
Mid Frequency, Hz | 125 | 250 | 500 | 1000 | 2000 | 4000
NC Drivers | [7 empty] | NC= M1*Band Spl+ Intcpt
Intcpt | -31.6 | -18.9 | -8.5 | -2.2 | 1 | 3.1
M1 | 1.28 | 1.18 | 1.09 | 1.02 | 1 | 0.98
Lined Duct
Constants | 125 | 250 | 500 | 1000 | 2000 | 4000 |  | dB/ft = 10^C1 * p/a^C2 * t^C3
C1 | -0.865 | -0.582 | -0.0121 | 0.298 | 0.089 | 0.0649 |  | where :
C2 | 0.723 | 0.826 | 0.487 | 0.513 | 0.862 | 0.629 |  | p/a = 2*(Width+Height)/(Width*Height)*12, in inches |  |  |  | Application Reductions
C3 | 0.375 | 0.975 | 0.868 | 0.317 | 0 | 0 |  | t = lining thickness, in. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Flex Duct
Constants | 125 | 250 | 500 | 1000 | 2000 | 4000 |  | IL, by Band = (C1+C2*Dia+C3*Dia^2) + ((C4+C5*Dia+C6*Dia^2)*Length)
C1 | 2.601 | -2.0231 | 1.5331 | 23.452 | 26.1549 | 25.06 |  | Diameter in inches, Length in feet
C2 | -0.12506 | 1.2762 | 1.4076 | -2.8449 | -2.8852 | -4.0431 |  |  | Edited 11/19/2008 to make totals the same as the -98 version. DIH
C3 | -0.0063392 | -0.082116 | -0.083166 | 0.085175 | 0.088421 | 0.16269
C4 | 0.48524 | -0.69143 | 1.9482 | 0.83804 | 1.7025 | 0.22397
C5 | 0.077579 | 0.43784 | 0.062717 | 0.3255 | 0.16157 | 0.34437
C6 | -0.0052214 | -0.020816 | -0.0050562 | -0.014685 | -0.0099562 | -0.020039
Elbows, 11-20 " Wide (use Avg = 15")
Elbow Type | 125 | 250 | 500 | 1000 | 2000 | 4000
kHz* avg. width | 1.875 | 3.75 | 7.5 | 15 | 30 | 60
1, Lined Rectangular | 1 | 6 | 6 | 11 | 10 | 10 |  | Excerpted from tables D11,12, ARI 885-98
2, Lined rect, Turning Vanes | 1 | 4 | 4 | 7 | 7 | 7 |  | Using tables below, and freq (in Khz) * Width, the followong tables apply
3, Unlined Rectangular | 1 | 5 | 5 | 8 | 4 | 3
4, Unlined Round | 1 | 2 | 2 | 3 | 3 | 3
Basis of table | Type 1 |  | Type 2 |  | Type 3 |  | Type 4 |  |  | Hz at 15" width (mean)
Hz | Loss | fw | Loss | fw | Loss | fw | Loss | fw |  | Loss from ARI 885-98
125 | 1 | 1.9-3.8 | 1 | 1.9-3.8 | 1 | 1.9-3.8 | 1 | 1.9-3.8
250 | 6 | 3.8-7.5 | 4 | 3.8-7.5 | 5 | 3.8-7.5 | 2 | 3.8-7.5
500 | 11 | 7.5 - 15 | 7 | >15 | 8 | 7.5 - 15 | 3 | >7.5
1000 | 10 | >15 |  |  | 4 | 15-30
2000 |  |  |  |  | 3 | >30
Tees, 11-20 " Wide | [7 empty] | Same as above, plus 3db for I split
Elbow Type | 125 | 250 | 500 | 1000 | 2000 | 4000
1, Lined Rectangular | 4 | 9 | 9 | 14 | 13 | 13
2, Lined rect, Turning Vanes | 4 | 7 | 7 | 10 | 10 | 10
3, Unlined Rectangular | 4 | 8 | 8 | 11 | 7 | 6
4, Unlined Round | 4 | 5 | 5 | 6 | 6 | 6
End Reflection
| C0 | 1127 | Speed of sound , f/second
| Pi | 3.1416 | Pi | [5 empty] | ERL (From ASHRAE RP 1314) ERL = 10*Log(1+(a1*c/Pi*f*(D/12))^a2)
| a1 | 0.7 | a1, flush - Terminated duct, Pink Noise, full octave | [5 empty] | Where F = octave band frequency.
| a2 | 2 | a2, flush - Terminated duct, Pink Noise, full octave, rounded | [5 empty] | D in inches
ARI 885-98 / Radiated, combined ceiling plenum/space effect | [10 empty] | 788.9
Ceiling/Plenum Effect Attenuation Values, Radiated sound | [7 empty] | Table from ARI standard |  |  | 327.249
Tile Type | 125 | 250 | 500 | 1000 | 2000 | 4000 |  |  |  |  | 2.4107
1, Mineral Fiber | 16 | 18 | 20 | 26 | 31 | 36 |  |  |  |  | 5.8115
2, Mineral Fiber | 15 | 17 | 19 | 25 | 30 | 33 |  |  |  |  | 6.8115
3, Glass Fiber | 16 | 15 | 17 | 17 | 18 | 19 |  |  |  |  | 0.83324
4, Glass Fiber | 17 | 18 | 21 | 25 | 29 | 35 |  |  |  |  | 8.3324
5, Glass Fiber, TL Backed | 17 | 18 | 22 | 27 | 32 | 39
6, Gypsym Board Tiles | 16 | 18 | 18 | 21 | 22 | 22
7, Solid Gypsum Board | 21 | 25 | 25 | 27 | 27 | 28
8, Solid Gypsum Board | 23 | 27 | 27 | 29 | 29 | 30
9, Double Gypsum Board | 27 | 31 | 31 | 33 | 33 | 34
10, Double Gypsum Board | 29 | 33 | 33 | 35 | 35 | 36
11, Concealed Spline | 23 | 24 | 24 | 29 | 33 | 34
Space Effect, Point Source | [7 empty] | Shultz equation
Log Distance, ft. | 10 | [6 empty] | Room SPL = Sound Power less (10 * Log(Distance) + 5 * Log(Volume)+ 3 * Log(Freq[I]) - 25)
Log Room Volume, CuFt | 5
Log Frequency, Hz | 3
Constant | 25
Environmental Adjustment Factor
Standard referenced | 125 | 250 | 500 | 1000 | 2000 | 4000
ARI 885-90 | 3 | 2 | 1 | 1 | 1 | 1
ARI 885-98 | 2 | 1 | 0 | 0 | 0 | 0

## NC_Source
WRITTEN BY: TARSHA L. SIMON |  |  |  |  | DATE: Jan 17, 1991
MODIFIED BY: D Int-Hout, 2/95
NCPLOT |  |  |  |  | RC Data
|  | -2 |  |  | 50
|  | -1 |  |  | 45
| 32 | 0 |  | 0 | 40
NC15 | 63 | 1 | 47 | 1 | 35
| 125 | 2 | 36 | 2 | 30
| 250 | 3 | 29 | 3 | 25
| 500 | 4 | 22 | 4 | 20
| 1000 | 5 | 17 | 5 | 15
| 2000 | 6 | 14 | 6 | 10
| 4000 | 7 | 12 | 7 | 5
|  | 8 |  |  | 0
|  | -1 |  |  | 50
| 32 | 0 |  |  | 45
NC20 | 63 | 1 | 51 |  | 40
| 125 | 2 | 40 |  | 35
| 250 | 3 | 33 |  | 30
| 500 | 4 | 26 |  | 25
| 1000 | 5 | 22 |  | 20
| 2000 | 6 | 19 |  | 15
| 4000 | 7 | 17 |  | 10
|  | 8 |  |  | 5
|  | -1 |  |  | 55
| 32 | 0 |  |  | 50
NC25 | 63 | 1 | 54 |  | 45
| 125 | 2 | 44 |  | 40
| 250 | 3 | 37 |  | 35
| 500 | 4 | 31 |  | 30
| 1000 | 5 | 27 |  | 25
| 2000 | 6 | 24 |  | 20
| 4000 | 7 | 22 |  | 15
|  | 8 |  |  | 10
|  | -1 |  |  | 60
|  | 0 |  |  | 55
NC30 | 63 | 1 | 57 |  | 50
| 125 | 2 | 48 |  | 45
| 250 | 3 | 41 |  | 40
| 500 | 4 | 35 |  | 35
| 1000 | 5 | 31 |  | 30
| 2000 | 6 | 29 |  | 25
| 4000 | 7 | 28 |  | 20
|  | 8 |  |  | 15
|  | -1 |  |  | 65
|  | 0 |  |  | 60
NC35 | 63 | 1 | 60 |  | 55
| 125 | 2 | 52 |  | 50
| 250 | 3 | 45 |  | 45
| 500 | 4 | 40 |  | 40
| 1000 | 5 | 36 |  | 35
| 2000 | 6 | 34 |  | 30
| 4000 | 7 | 33 |  | 25
|  | 8 |  |  | 20
|  | -1 |  |  | 70
|  | 0 |  |  | 65
NC40 | 63 | 1 | 64 |  | 60
| 125 | 2 | 56 |  | 55
| 250 | 3 | 50 |  | 50
| 500 | 4 | 45 |  | 45
| 1000 | 5 | 41 |  | 40
| 2000 | 6 | 39 |  | 35
| 4000 | 7 | 38 |  | 30
|  | 8 |  |  | 25
|  | -1 |  |  | 75
|  | 0 |  |  | 70
NC45 | 63 | 1 | 67 |  | 65
| 125 | 2 | 60 |  | 60
| 250 | 3 | 54 |  | 55
| 500 | 4 | 49 |  | 50
| 1000 | 5 | 46 |  | 45
| 2000 | 6 | 44 |  | 40
| 4000 | 7 | 43 |  | 35
|  | 8 |  |  | 30
|  | -1 |  |  | 80
|  | 0 |  |  | 75
NC50 | 63 | 1 | 71 |  | 70
| 125 | 2 | 64 |  | 65
| 250 | 3 | 58 |  | 60
| 500 | 4 | 54 |  | 55
| 1000 | 5 | 51 |  | 50
| 2000 | 6 | 49 |  | 45
| 4000 | 7 | 48 |  | 40
|  | 8 |  |  | 35
|  | -1 |  |  | 85
|  | 0 |  |  | 80
NC55 | 63 | 1 | 74 |  | 75
| 125 | 2 | 67 |  | 70
| 250 | 3 | 62 |  | 65
| 500 | 4 | 58 |  | 60
| 1000 | 5 | 56 |  | 55
| 2000 | 6 | 54 |  | 50
| 4000 | 7 | 53 |  | 45
|  | 8 |  |  | 40
|  | -1 |  |  | 90
|  | 0 |  |  | 85
NC60 | 63 | 1 | 77 |  | 80
| 125 | 2 | 71 |  | 75
| 250 | 3 | 67 |  | 70
| 500 | 4 | 63 |  | 65
| 1000 | 5 | 61 |  | 60
| 2000 | 6 | 59 |  | 55
| 4000 | 7 | 58 |  | 50
|  | 8 |  |  | 45
|  | -1 |  |  | 95
|  | 0 |  |  | 90
NC65 | 63 | 1 | 80 |  | 85
| 125 | 2 | 75 |  | 80
| 250 | 3 | 71 |  | 75
| 500 | 4 | 68 |  | 70
| 1000 | 5 | 66 |  | 65
| 2000 | 6 | 64 |  | 60
| 4000 | 7 | 63 |  | 55
|  | 8 |  |  | 50
|  | -1 | 78 |  | 78
|  | 0 | 58 |  | 58
HEARING THRESHOLD |  | 1 | 36 |  | 36
|  | 2 | 22 |  | 22
|  | 3 | 13 |  | 13
|  | 4 | 8 |  | 1
5
6
7
8